SECTION 09 69 00 – ACCESS FLOORING – 2500 System No Underfloor Air

- GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

This Section includes the following:

Interchangeable access-flooring panels

Understructure

Labor, material, equipment and installation as per specifications and/or shown on the Architect’s drawings.

Related Sections include the following:

Section 03 30 00 – Concrete work and concrete floor sealer

Concrete sealer and pedestal adhesive must be chemically compatible with each other.

Section 09 68 00 – Carpet and carpet tile work

Section 23 30 00 – Mechanical air distribution

Section 26 05 00 – Electrical connections and grounding

PERFORMANCE REQUIREMENTS

Provide access flooring system consisting of moveable assemblies composed of modular floor panels supported on pedestals forming accessible under floor cavities to accommodate electrical, mechanical, and HVAC services which comply with performance requirements specified. Raised floor panels must be interchangeable with each other except where cut for special conditions.

Where applicable load testing shall be performed according to “Recommended Test Procedures for Access Flooring” as established by the Ceiling and Interior Systems Construction Association (CISCA). These procedures shall be used as a guideline when presenting load performance product information.

Concentrated Load: 2500 lb. on one square inch (25mm) load at any location with a top surface deflection not to exceed 0.10" (2.5mm) and a permanent set not to exceed .010” (.25mm).

Uniform Load: With a top surface deflection not exceeding 0.040” (1mm), TecCrete can hold 900 pounds per square foot evenly distributed over the surface of the panel with a permanent set not exceeding 0.010” (0.25mm).

Ultimate Load: Panel shall be designed to withstand a load of 3100 lb. applied over one inch at the weakest point on a stringer.

Rolling Load: Panels shall withstand a rolling load of 2000 lbs. applied through a 3" dia. (76mm) x 1-13/16" (46mm) wide caster for 10 cycles over the same path with less than 0.040” top surface permanent set. Panels shall withstand a rolling load of 2000 lb. applied through a hard rubber-surfaced wheel 10” (254mm) dia. x 4” (102mm) wide for 10,000 cycles over the same path.  Permanent set at the conclusion of the test shall not exceed .040” (1mm).

Impact Load: A 150 lb. load dropped from 36"(914mm) onto a one-inch square indenter shall not render the system unserviceable.

Flammability: Bare panel system shall meet Class A requirements for Flame spread and smoke development when tested in accordance with ASTM-E84 and a maximum Flame spread of 25, Smoke development of 50 based on the average of three runs when tested in accordance with CAN/ULC S102.

Combustibility: All components of the access floor system shall qualify as noncombustible by demonstrating compliance with requirements of ASTM E 136, Standard Test Method for Behavior of Materials in a Vertical Tube Furnace at 750 degrees C.

Recycled Content: Panel and understructure system shall be required to have a minimum recycled content of 50%.

Pedestal Axial Load Test: Provide pedestal assemblies without panels or other supports in place, capable of withstanding a 6000 lb. (26,689 N) Axial load per pedestal, according to CISCA A/F, Section 5 “Pedestal Axial Load Test.”

Verify requirements for pedestal overturning moment in seismic zones with authorities having jurisdiction. Coordinate with pedestals selected in Part 2 and method of attachment specified.

Pedestal Overturning Moment Test: Provide pedestal assemblies, without panels or other supports in place, capable of withstanding an average overturning moment of 1000 in*lbs. (113 N*m) when bonded to clean concrete slab according to CISCA A/F, Section 6, “Pedestal Overturning Moment Test.”

Product testing shall be witnessed and certified by an accredited independent engineering and testing laboratory based in the U.S.A. with a minimum of five (5) years’ experience testing access floor components in accordance with CISCA test methods.

COUNTRY OF ORIGIN

Access floor materials shall comply with the provisions outlined in FAR Subpart 25.2–Buy American Act–Construction Materials.

SUBMITTALS

Submit a sample of the floor panel and each understructure component.

Shop Drawings:

Submit drawings showing raised floor panel layout including starting point of installation.

Include details of component panels and pedestals. If required show edge details of ramps, steps, handrails and anchoring of pedestal bases to subfloor.

Product Certificates:

Submit independent testing organization certificates indicating compliance with specified design criteria when tested and reported according to CISCA “Recommended Test Procedures for Access Floors.”

Submit seismic calculations if required in accordance with local and state building codes as specified. Calculations shall be performed using a current seismic program and submitted to a local structural engineer licensed in the state where the project is located. The structural engineer shall sign and seal these calculations confirming that these calculations meet all local and state codes for seismic pedestal assemblies. A signed copy of these calculations must be given to the architect and local building department as required.

QUALITY ASSURANCE

Manufacturer Qualifications:

All primary products specified in this section will be supplied by a single manufacturer with a minimum of ten (10) years’ experience and is ISO 9001:2015 certified, demonstrating a well-documented quality management system.

Manufacturer facilities shall be ISO 14001:2015 certified, demonstrating that they maintain an environmental management system.

Installer Qualifications: Engage an experienced installer with minimum of 5 years’ experience in the installation of access floor systems of comparable size and complexity.

Access Floor Tolerances:

Manufacturing Tolerance:

        - Panel flatness (measured on the diagonal): ± 0.040" (1mm) or less.

        - Panel flatness (measured on edge of pan): ± 0.030" (.8mm) or less.

        - Panel squareness: ± 0.030" (.8mm) or less.

        - Panel interchangeability: All panels, except those modified to meet special conditions, shall be interchangeable.

Installation Tolerance:

        - Finished installation shall be level within ± 0.060" (2mm) in 10 feet (3m) and ± 0.100" (3mm) for the entire floor.

DELIVERY STORAGE AND HANDLING

Deliver flooring components clearly labeled with manufacturer’s name and item description.

Handle and store packages containing flooring in a manner which avoids overloading building structure.

The General Contractor and or owner shall provide a dry accessible area to receive and unload material with a free path to elevators, hoists and/or the area receiving the floor.

The subfloor shall be free of moisture, dust, dirt and other debris. Once installed, the tile floor must be maintained in the same manner.

PROJECT CONDITIONS

The General Contractor and/or Owner shall provide a clean, level, dry subfloor, temperature controlled, and protected from the weather.

Access flooring storage and installation areas shall be maintained at a temperature between 40°F to 120°F and be less than 70% relative humidity for 24 hours a day before, during and after installation.

Overhead construction work must be completed before installing access floor to avoid damage to panels and finishes. Any damage to panels or finishes resulting from construction work done after floor is installed shall be the responsibility of the general contractor.

- PRODUCTS

MANUFACTURERS

Basis-of-Design Product: Subject to compliance with requirements, provide Global IFS; [TecCrete Access Flooring], located in Grand Rapids, MI 49512.

Substitutions will be considered, providing the alternative products meet or exceed the feature requirements as indicated herein and the performance requirements including the rolling load as outlined in section 1.3 and receive prior written approval by the Architect. The manufacturer shall certify that all panels meet or exceed the stated design criteria.

MATERIALS

Floor Panels: TecCrete 2500 lb. Panels shall be integrated steel pan construction with exposed top surface of lightweight concrete fill. Floor Panels are bare corner-lock.

      - Panels shall be nominal 24” (610mm) square x 1 ½” (38mm) deep, manufactured with galvannealed steel pan having shear tabs that integrally bond to the lightweight, high-strength concrete fill. Panel corners shall be manufactured to receive the pedestal head positioning dome. Each panel shall accept a flush-fit metal fastener which securely fastens each panel corner to the pedestal head.

Panel Finish: Floor panel surface shall be factory standard bare concrete for field installed carpet tile. Panels shall have a maximum electrical resistance of 10 ohms or less from the top edge of the panel, less surface covering, to the understructure.

Air Supply Panels:

Provide and/or install passive floor diffusers with factory cutouts as indicated on drawings.

Factory cut-outs shall be <centered> <quadrant> as shown. Panels with cutouts that are located in traffic areas as shown on the drawings shall have extra pedestal assemblies under the panel to support the cutout.

For underfloor air applications, provide air strip gaskets for exposed concrete panels, or high-pressure air highways, as indicated.

Understructure:

Pedestal assemblies shall be of hot-dip galvanized steel.

The base shall be a minimum of 16 square inches and shall be stamped and/or embossed on its underside and shall be adhered to the sub floor with an adhesive recommended by the access flooring manufacturer.

Where mechanical anchors are required for seismic zones, provide same as required by project specific seismic calculations.

The threaded stud shall be 3/4" (19mm) diameter steel.

The head assembly shall be designed so that the panels will be held in place with or without corner-lock fasteners.

Pedestal assembly shall provide an adjustment range of +/- 1” (25mm) when finished floor height is 6” (152mm) or more, adjustable at 1/64" (.4mm) increments.

The assembly shall provide a mechanical means to lock the floor in a level plane and adjustments shall be capable of being made without special tools.

For corner-lock system, the head of the all-steel assembly shall be designed to accept a metal fastener to mechanically lock the panels in place.

Pedestal assembly shall support not less than 6,000 lb. axial load and shall resist an average 1,000 inch-pound overturning moment when bonded to a clean concrete slab.

Heavy Duty Stringers:

Stringer shall capture panels and be capable of supporting a 450-lb. concentrated load at mid span with less than 0.010” (0.25mm) permanent set after the load is removed.

Stringers shall be individually and rigidly fastened to the pedestal with one machine screw for each foot of stringer length. Bolts shall provide positive electrical contact between the stringers and pedestals. Connections depending on gravity or spring action are unacceptable.

Stringer shall be either 2’x 2’ or 4’x 4’ pattern and shall be secured by a fastener.

Accessories:

Furnish ramps, steps, lateral bracing, fascia, handrails, cutouts and miscellaneous items where indicated.

- EXECUTION

INSPECTION

Examine the subfloor which is to receive access flooring for dryness, cleanliness, unevenness, or any irregularities that will affect the quality of the access flooring.

Verify that material storage and installation areas are at recommended temperature and relative humidity before, during, and after installation.

Verify that access floor is level to within 1/8” (3mm) in 10 feet (3m).

Do not commence installation of access flooring until subfloor is clean and dry, temperature controlled, and protected from the weather.

INSTALLATION

Pedestal locations shall be established from approved shop drawings so that mechanical and electrical work can be installed without interfering with pedestal locations.

Installer is to coordinate with other trades to maintain the integrity of the installed access flooring. All traffic on access floor shall be controlled by the installer only. No traffic other than the access floor installation crew shall be permitted on any floor area for 48 hours to allow the pedestal adhesive to set. Access floor panels shall not be removed by other trades for 72 hours after their installation.

Floor system and accessories shall be installed by an authorized factory trained installation company with a minimum of five (5) years’ experience.

No dust or debris producing operations by other trades shall be allowed in areas where access floor is being installed to ensure proper bonding of pedestals to subfloor.

Installer shall keep the subfloor broom clean as installation progresses.

Install floor diffusers if required as indicated on Mechanical Plans.

Finished installation shall be level within +/- 0.060” (2mm) in 10 feet (3m) and +/- 0.100” (3mm) for the entire floor area.

Replace damaged materials prior to the application of field applied surfaces.

The General Contractor or Subcontractor shall assure compatibility between the concrete sealer and the pedestal adhesive provided by the access floor manufacturer.

ACCEPTANCE

General Contractor or Owner shall accept completed access floor in whole or in part, prior to allowing other trades to perform work which affects the installed access floor.

General Contractor shall suitably protect the accepted access floor and accessories from damage, contamination or overloading.

The General Contractor shall be responsible for the final underfloor cleaning.

END OF SECTION 09 69 00